## Tasks
name | active
Bright Sunlight | TRUE
Working on a ground array | TRUE
Extreme cold | TRUE
Extreme heat | TRUE
Ladder access | TRUE
Loading/off Loading LANDSCAPE Trailer | TRUE
Loading/off Loading TRACTOR Trailer | TRUE
Scissor Lift Roof Access | TRUE
Using a Crane to move materials | TRUE
Using a telehandler to move materials | TRUE
Working at height flat roof | TRUE
Electrically isolating solar panels | TRUE
Mechanically removing/attaching solar panels | TRUE
Working in an inverter | TRUE
Working in a DC Combiner | TRUE
IR viewing panels | TRUE

## Hazards
task | category | risk | barriers | mit | active
Extreme heat | Extreme heat/cold | Medium | 9. Supervisor/observer | Keep an eye on the people around you, look for signs of heat stroke | TRUE
Extreme heat | Extreme heat/cold | Medium | 1. Eliminate the hazard/threat | Shift to an earlier work day | TRUE
Extreme heat | Extreme heat/cold | Medium | 1. Eliminate the hazard/threat | Take breaks in shady area | TRUE
Extreme heat | Hot surfaces | Medium | 4.PPE | Roof surfaces, especially dark ones can become very hot. Wear gloves that are thick enough to insulate from heat. | TRUE
Extreme cold | Extreme heat/cold | Medium | 9. Supervisor/observer | Keep an eye on the people around you, look for cold stress symptoms | TRUE
Extreme cold | Electrical contact | Medium | 1. Eliminate the hazard/threat; 4. PPE | Wear layers, make sure cold weather clothing does not compromise arc protective clothing | TRUE
Extreme cold | Extreme heat/cold | Medium | 1. Eliminate the hazard/threat | Delay work if reduced dexterity will affect job safety | TRUE
Bright Sunlight | UV exposure | High | 4. PPE | Wear safety glasses rated to block UV | TRUE
Bright Sunlight | UV exposure | Medium | 4. PPE | Use sweat resistant sunblock on all exposed skin, re-apply per manufacturer instructions | TRUE
Scissor Lift Roof Access | Vehicle instability | High | 1. Eliminate hazard; 5. Warning Device; 8. Training | Only allow employees certified by AEPS to drive lifts, setup on solid ground, use outriggers, do not override tilt alarms | TRUE
Scissor Lift Roof Access | Equipment failure | Medium | 5. Warning Device; 8. Training | Inspected daily. Equipment must be put out of service immediately if warning lights are lit or machine damage is evident | TRUE
Scissor Lift Roof Access | Traffic collisions | High | 3. Physical Barriers; 5. Warning Device | Use cones to mark out work area around stationary lifts, walkers required when lift is moving | TRUE
Scissor Lift Roof Access | Falling from height | High | 3. Physical Barriers | Remain aware at all times when in basket, keep entire body inside of basket railing | TRUE
Scissor Lift Roof Access | Electrical contact | High | 8. Training | Be aware of what is around and above scissor lift when operating, especially power lines | TRUE
Ladder access | Equipment failure | High | 1. Eliminate hazard; 6. Minimize error; 8. Training | Ladders inspections need to be done daily and they should be put out of use at first sign of failure, never erect a ladder over a doorway | TRUE
Ladder access | Falling from height | High | 4. PPE; 8. Training | Erect Ladders on stable footings, correct angle, tied up, not used past usable reach, 3ft above landing surface | TRUE
Ladder access | Climbing | High | 6. Minimize error; 8. Training | Maintain 3 points of contact when climbing ladders — no carrying material or tools up ladders | TRUE
Ladder access | Falling objects | High | 3. Physical Barriers; 4.PPE; 8. Training | Only one worker is allowed on a ladder at a time, cones should be in place to keep people from walking under ladders were they could be struck by falling objects. | TRUE
Working at height flat roof | Falling from height | High | 4.PPE; 8. Training | Inspect work area, including access and egress points, for holes, damdged roof deck areas, and skylights. Baracade off areas of concern and notify crew members. | TRUE
Working at height flat roof | Damage to building contents | Medium | 8. Training | If a potential leak point is created, or pre-existing, mark it with an oil pencil, enter it in SF, and report to the work manager | TRUE
Working at height flat roof | Falling from height | High | 3. Physical Barriers; 4. PPE; 8. Training | Use guardrails, safety monitor, and warning lines where feasible — fall arrest systems if called for | TRUE
Working at height flat roof | Falling objects | High | 1. Eliminate hazard; 9. Supervisor/observer | Stow material and tools safely, be particularly careful when working near the edge of the roof | TRUE
Working at height flat roof | Falling objects | High | 3. Physical Barriers | Be aware of pedestrians and workers on the ground. Restrict access to base of building under work area using cones and tape | TRUE
Working on a ground array | Slippery areas | Medium | 6. Minimize chances of error | Watch for uneven turane, trip fall hazards covered by grass | TRUE
Working on a ground array | Poisonous/dangerous animals | Medium | 1. Eliminate the hazard/threat | Spray deet based bug spray, following product directions, especially around pants and shoes to reduce the possibility of tick bites. | TRUE
Working on a ground array | Traffic collisions | Medium | 6. Minimize chances of error; 8. Training | Drive slowly and cautiously when driving a vehicle inside of a ground array, obsticles, uneven terrain, and wet ground can be hidden by ground cover | TRUE
Working on a ground array | Forest fires | High | 1. Eliminate the hazard/threat; 8. Training | Be extra careful of igniting dry grass, SMOKING IS NOT ALLOWED INSIDE OF A GROUND ARRAY! | TRUE
Working on a ground array | Disturbing wildlife | Medium | 9.Supervisor/observer | Be aware of the animals in the surounding habitat and their needs. Our goal is to impact the environment as little as possible. | TRUE
Working on a ground array | Change in normal/natural draining/flow patterns | Medium |  | Be aware of storm water flow patterns when moving dirt, or plants | TRUE
Working on a ground array | Erosion | Medium |  | Plan for the potential of newly disturbed dirt to erode. Be particularly careful to protect streams and other waterways from dirt erosion. Call Project Manager with quesitons/concerns | TRUE
Using a telehandler to move materials | Vehicle instability | High | 6. Minimize error; 8. Training | Only allow employees certified by AEPS to drive lifts, setup on solid ground, use outriggers, do not override tilt alarms. Follow lift tables, drive slowly | TRUE
Using a telehandler to move materials | Equipment failure | High | 8. Training | Inspect telehandlers daily, and put out of service immediately if warning lights are lit or machine damage is evident | TRUE
Using a telehandler to move materials | Shifting loads | High | 6. Minimize error; 8. Training | Balance and secure loads, carry loads as low to the ground as possible | TRUE
Using a telehandler to move materials | Falling from height | High | 3. Physical Barriers; 5. Warning Device; 8. Training | Cordon off roof loading area to comply with proper fall protection and make sure that staging does not interfere with roof egress | TRUE
Using a telehandler to move materials | Falling structures | High | 8. Training; 9. Supervisor/observer | Ensure that the roof structure is sound AND approved for maximum point and total load before loading materials onto it | TRUE
Using a telehandler to move materials | Falling structures | High | 8. Training; 9. Supervisor/observer | Place loads on roof support members close to the intersection of I beams, or support walls | TRUE
Using a telehandler to move materials | Falling objects | High | 4.PPE; 8. Training | Keep hard hats on! Telehandler driver must watch for pedestrians, but pedestrians must also watch for telehandler. Use cones, flag walkers when needed | TRUE
Using a Crane to move materials | Overhead cranes | High | 6. Minimize chances of error; 9.Supervisor/observer | Crane opperating company has primary responsibility for rigging, and craning safety, however, anyone can stop a craning activity if they do not feel that it is progressing safely! | TRUE
Using a Crane to move materials | Falling objects | High | 1. Eliminate the hazard/threat; 6. Minimize chances of error; 9.Supervisor/observer | Confirm the maximum potential weight being picked with crane operator. Craning crew should be using their own rigging equipment! | TRUE
Using a Crane to move materials | Falling objects | High | 3. Physical Barriers; 5. Warning Device; 8. Training | Keep craned loads from traveling over persons — use cones, caution tape, monitors, and communication with building occupants | TRUE
Using a Crane to move materials | Overhead cranes | Medium | 6. Minimize error; 8. Training | Reminded AEPS Employees of the weight of a crane pick load and told not to go near or touch a load that is in the air | TRUE
Using a Crane to move materials | Electrical contact | Medium | 1. Eliminate hazard; 5. Warning Device; 9. Supervisor/observer | Ensure that craning team is aware of all electrical power lines that could interfere with their craning activity | TRUE
Using a Crane to move materials | Falling structures | High | 8. Training; 9. Supervisor/observer | Vissually check that the roof structure is sound AND approved for maximum point and total load before loading | TRUE
Using a Crane to move materials | Falling structures | High | 8. Training; 9. Supervisor/observer | Place loads on roof support members close to the intersection of I beams, or support walls | TRUE
Loading/off Loading TRACTOR Trailer | Falling objects | High | 1. Eliminate hazard; 6. Minimize error | Employees should distance themselves from loads being moved — palletized materials can shift and fall when being loaded | TRUE
Loading/off Loading TRACTOR Trailer | Vehicle instability | Medium | 4. PPE; 8. Training | Forklifts and telehandlers become less stable as loads are lifted higher. Be extra careful on uneven or sloped terrain and wear seatbelts | TRUE
Loading/off Loading TRACTOR Trailer | Rigging failure | High | 1. Eliminate hazard; 6. Minimize error | Ensure that material pallets are stacked straight, not too high, and material is secured to pallet | TRUE
Loading/off Loading TRACTOR Trailer | Shifting loads | High | 1. Eliminate hazard; 6. Minimize error | Do not double-stack pallets without a supervisor approval | TRUE
Loading/off Loading TRACTOR Trailer | Traffic collisions | Medium | 3. Physical Barriers; 5. Warning Device; 9. Supervisor/observer | Cordon off loading/unloading areas with cones and/or tape, use a spotter | TRUE
Loading/off Loading TRACTOR Trailer | Traffic collisions | High | 4. PPE; 9. Supervisor/observer | Everyone working around the loading area must wear high visibility clothing | TRUE
Loading/off Loading TRACTOR Trailer | Falling objects | High | 8. Training | We are not experts in tractor trailer load management or lashing. The truck operator must decide on load placement and secure their own load | TRUE
Loading/off Loading LANDSCAPE Trailer | Equipment failure | High | 6. Minimize error; 8. Training | AEPS truck driver sould personally inspect trailer for safety and correct operation before loading | TRUE
Loading/off Loading LANDSCAPE Trailer | Falling objects | High | 1. Eliminate the hazard/threat; 6. Minimize chances of error | Employees should distance themselves from the loads being moved, understanding that paletized materials can shift and fall when being loaded. | TRUE
Loading/off Loading LANDSCAPE Trailer | Vehicle instability | Medium | 4.PPE; 8. Training | Forklifts and telehandlers can become less stable the higher loads are lifted. Be extra careful opperating on uneven or sloped terran and wear seatbelts! | TRUE
Loading/off Loading LANDSCAPE Trailer | Rigging failure | High | 1. Eliminate the hazard/threat; 6. Minimize chances of error | Ensure that materials pallets are stacked straight, and not too high to be stable, and material is secure to palet adequately | TRUE
Loading/off Loading LANDSCAPE Trailer | Shifting loads | High | 1. Eliminate the hazard/threat; 6. Minimize chances of error | Do not doublestack pallets, without a suppervisor's approval. | TRUE
Loading/off Loading LANDSCAPE Trailer | Traffic collisions | Medium | 3. Physical Barriers; 5. Warning Device; 9.Supervisor/observer | Cordone off loading/unloading areas with cones and/or tape | TRUE
Loading/off Loading LANDSCAPE Trailer | Traffic collisions | High | 4.PPE; 9.Supervisor/observer | Everyone working around the loading area must wear high visability clothing | TRUE
Loading/off Loading LANDSCAPE Trailer | Shifting loads | High | 6. Minimize chances of error; 8. Training | AEPS truck driver has final responsibility for ensuring that the load is lashed down, balanced - inspect carefully before pulling away! | TRUE
Electrically isolating solar panels | Electrical contact | High | 2. Minimize Energy to Safe Level; 4.PPE; 8. Training | Qualified person(s) should open COMBINER BOX disconnects, then open string fuses, then LOTO combiner boxes where strings terminate. | TRUE
Electrically isolating solar panels | Electrical contact | High | 2. Minimize Energy to Safe Level; 4.PPE; 8. Training | Qualified person(s) should open STRING INVERTER disconnects, then LOTO the inverter DC disconnect. | TRUE
Electrically isolating solar panels | Electrical contact | High | 5. Warning Device; 8. Training | Qualified person(s) should check string with a clamp-on multimeter before opening | TRUE
Electrically isolating solar panels | Electrical contact | High | 5. Warning Device; 8. Training | Do not disconnect module leads until confirming that there is no current on the string via a clamp-on multimeter | TRUE
Mechanically removing/attaching solar panels | Electrical contact | High | 1. Eliminate the hazard/threat | Follow guidelines for electrically isolating solar panels before removing or re-installing solar panels | TRUE
Mechanically removing/attaching solar panels | Cuts / bleeding | Medium | 4.PPE; 8. Training | Cracked module surfaces can be very sharp, make sure to wear adequate gloves, and clothing to keep the surface away from your skin | TRUE
Mechanically removing/attaching solar panels | Falling objects | High | 6. Minimize chances of error; 8. Training | User torque tool to ensure that panel fasteners are installed to manufacturer specified torque. | TRUE
Mechanically removing/attaching solar panels | Muscle Fatique | Medium | 8. Training | Follow NIOSH guidelines and limit single person lifting to under 51lbs | TRUE
Mechanically removing/attaching solar panels | Falling objects | Medium | 6. Minimize chances of error; 8. Training | Do not carry modules around in higher wind | TRUE
Mechanically removing/attaching solar panels | Falling objects | High | 1. Eliminate the hazard/threat; 8. Training | Secure materials and tools as you work. Never leave unsecured materials unnatended. Wind can pickup sudddenly. | TRUE
Working in an inverter | Electrical contact | High | 6. Minimize chances of error; 9.Supervisor/observer | ONLY QUALIFIED PERSONS SHOULD BE WORKING INSIDE OF AN INVERTER! | TRUE
Working in an inverter | Electrical contact | High | 3. Physical Barriers; 4.PPE | Follow LOTO process to disconnect inverter from AC power source, and then confirm AC power is disconnected at inverter. | TRUE
Working in an inverter | Electrical contact | High | 2. Minimize Energy to Safe Level | Be aware that capacitors in an inverter can store energy for 5 minutes or more before they dissapate! | TRUE
Working in an inverter | Electrical contact | High | 3. Physical Barriers; 4.PPE | Open COMBINER BOX disconnects and LOTO. dc busbar and all PV output circuits will be energized until all combiner disconnects are open. | TRUE
Working in an inverter | Electrical contact | High | 3. Physical Barriers; 4.PPE | Inverter DC and AC disconnects should be opened and LOTO before opening inverter | TRUE
Working in an inverter | Electrical contact | High | 3. Physical Barriers; 4.PPE | Be aware that lineside connections on the INTERNAL inverter dc and ac disconnects will remain energized unless all ac and dc sources are removed | TRUE
Working in a DC Combiner | Electrical contact | High | 6. Minimize chances of error; 9.Supervisor/observer | ONLY QUALIFIED PERSONS SHOULD BE WORKING INSIDE OF A dc COMBINER | TRUE
Working in a DC Combiner | Arching/electrical contact | High | 2. Minimize Energy to Safe Level; 5. Warning Device | Only open touch safe fuses after confirming that no current is running through the string with a clamp on amp meter | TRUE
Working in a DC Combiner | Electrical contact | High | 2. Minimize Energy to Safe Level; 8. Training | Combiner box disconnect should be open and LOTO, but THIS WILL NOT STOP POWER FROM ENTERING THE COMBINER FROM THE SOURCE STRINGS! | TRUE
Working in a DC Combiner | Backfeed | High | 3. Physical Barriers; 4.PPE | Issolated from other combiner boxes by opening the DC source circuit fuse in the inverter. | TRUE
Working in a DC Combiner | Electrical contact | High | 3. Physical Barriers; 4.PPE | Be aware that lineside connections on the INTERNAL combiner dc disconnect will remain energized unless panel sources are removed | TRUE
Working in a DC Combiner | Electrical contact | High | 3. Physical Barriers; 4.PPE | Be aware and test ground and grounded conductors for current | TRUE
IR viewing panels | Slippery areas | Medium | 8. Training | Stay aware of your surroundings, avoid looking through the IR cammera while walking | TRUE

## Personnel
name | role | phone | email | active
Michael Parker | Project Manager | 732-792-0700 x107 | mparker@aeps-electric.com | TRUE
Marvin Oyuela | Supervisor | 732-609-0997 |  | TRUE
Elieser Levon | Crew Leader | 347-855-9611 |  | TRUE
Carlos Medrano | Crew Leader | 346-946-1709 |  | TRUE
Daniel Torres | Crew Leader | 732-504-9248 |  | TRUE
Gregg Stephens | Director | 215-779-2789 |  | TRUE
Alexander Hoyos | Crew Member | 732-489-0968 |  | TRUE
Amhed | Crew Member |  |  | TRUE
Diego Maeda | Crew Member | 609-690-1449 |  | TRUE
Jorge Campos | Crew Member | 732-642-1376 |  | TRUE
Josue Ayala | Crew Member | 732-998-2607 |  | TRUE
Luis Marroquin | Crew Member | 732-867-4736 |  | TRUE

## Settings
Setting | Value
Company Name | AEPS-Electric
Form Title | HSSE Job Hazard Acknowledgment Form
Submit Email Address | safety@aeps-electric.com
Company Tagline
Office Phone | 732-792-0700
Save Folder | HSSE/Completed

## Instructions
AEPS HSSE Form E data workbook
Save in the Safety site > Shared Documents > HSSE as AEPS_HSSE_Data.xlsx.
Sheet names (Tasks, Hazards, Personnel, Settings) and the header row of each must not change.
To add an item, add a row. To retire one, set active to FALSE rather than deleting.
A hazard's 'task' must match a name on the Tasks sheet exactly.
Roles used by the form: Supervisor, Crew Leader, Director (Approved By); Crew Member and Crew Leader (crew sign-in list).
Keep notes and stray data off the four data sheets; the form reads every used cell.
Settings: 'Submit Email Address' and 'Save Folder' are used by the form.